Hardware Installation Guide

The Operations Team must follow the steps below

PRE-INSTALLATION:
1. Technical Reconnaissance (scope site layout & choose cabinet locations)
2. Plan the project (time-line, project lead, components needed, etc)
3. Start a hardware requisition
4. Order materials/components
5. Reconcile procurement of materials with project needs
6. Modify exiting hardware:
- Add holes for fans & wires
- Add block board to all cabinets covering the entire interior back wall of the cabinet

HOW TO CHOOSE CABINET LOCATIONS:

Pick a central location for the Switchboard:
- Distance between cabinet & workstations should not be > 100m
- If distance between any 2 points exceed 100m = add another switchboard cabinet

Switch
Cabinet

Choose a central location for the Server Cabinet:
- Needs to be in a well ventilated room, at least 1 window
- Room needs to be secure: windows with bars and door with locks

Choose a well ventilated area for the Power cabinet:
- Location should be close to ECSOM distribution board & safe from theft and weather conditions
- For J2's, if greater than 10 workstations = + 1 Power Cabinet (a full back up system with 4 batteries)

CABINET DESIGNS:

1
2
3

Standard Design = 3 cabinets. Switchboard + Server + Power

Alternative Design = 2 cabinets. (Switchboard + Server) + Power

CABINET LAYOUT

   NOT

Correct	Incorrect

STANDARD DESIGN
All cabinets in different rooms: see below

        Switchboard	+	Server	+	Power
Server
3

Fan(air out)
LVD

Charger

Power Connections

Shelf

Switch

4 Batteries

Power Connections

1

2
Fan(air out)
Blockboard
Fan(air in)
Blockboard
Voltage Monitor

Fan(air out)
Blockboard

ALTERNATIVE DESIGN

Server & Switchboard in the same cabinet stacked vertically on top of the Power Cabinet: see below

Switch
Server

Fan(air out)

+

Blockboard
1

        Switchboard & Server

Power Connections
2

Voltage Monitor

Blockboard

Fan (air out)
LVD

3

Charger)

4 Batteries
Shelf

        Power

Fan (air in)

Fan (air out)

Blockboard

DAY OF INSTALLATION

Should be done prior to Back Data Entry by Support & Deployment Team

Alternative Back Data Entry:The Support & Deployment Team connects touch-screens to a local server and ESCOM electricity, with a working hospital generator or Baobab generator, then migrate data later.

PRIOR TO DEPARTURE:
Use the “Hardware Check-list” to confirm you have all materials needed to bring to the site.

DAY 1: RUN WIRES & PIPES

1. Install PVC pipe for power connections (power cables for 48 volts inside)
2. Install PVC trunking (plastic covering) for Ethernet cables (connected to data socket)
3. Terminate Ethernet cables
4. Install data sockets (run cables to switchboard)

DAY 2: INSTALL CABINETS

1. Install Server cabinet
2. Install Switchboard cabinet
3. Install Power back up cabinet

DAY 3: TEST

1. Test Connectivity- use a laptop to test Ethernet connection to the site server (i.e. “ping” server IP addresses). Test point of care at each ward. Unsuccessful response = “host unreachable”
2. Test Power Connections with volt multimeter to make sure 48 volts are coming from each power socket that is connected to the four batteries in the power cabinet.
3. Install a data cable link (covered with PVC trunking) from the Baobab system to the HMIS system (i.e. their switchboard or computer in the HMIS office if the site does not have a network)
4. Test connectivity between Baobab system & HMIS office (i.e. “ping” server IP address)
5. If site has internet, configure Baobab server on site to access Baobab HQ server (“Cottonwood”)

SECURITY & SAFETY: FINAL CHECK

1. All cabinets must have a padlock
2. All rooms must be locked
3. Label keys: 1 set of with HMIS Officer & 1 set at Baobab HQ in Operations Department key cabinet
4. Every room with a power cabinet needs to have a fire extinguisher
Should not take more than 1 business week (5 days)

ENTER SUPPORT & DEPLOYMENT TEAM
Install Touch-screens
Run & Test Baobab module

OPERATIONS HARDWARE CHECKLIST	CHECK LIST FOR NEW SITE HW INSTALLATION
	TOOLS/ MATERIALS REQUIRED	QTY	CHECK
	Keys for server room & cabinets
	110V AC Transformer
	2.5mm earth wire
	48V cooling fan
	Babble level
	Bag of cement
	Batteries
	Battery Charger
	Battery charger for drill machine
	Battery terminals
	Blockboard
	Builder's knife
	Circuit Breaker
	Computer server
	Draw wire
	Drill bits ( concrete, steel, wood bits)
	Drill machines (both electric & battery power)
	Electric hacksaw
	File
	Fish tape
	Hacksaw
	Hammer
	Hydrolic cutting machine
	Insulation tape
	Key for drill chunk
	Ladders
	LVD
	Multimeter
	Network Switch
	Padlocks for cabinets
	Plain bend
	Pliers
	Power Extension cord
	PVC coupling
	PVC Nipples
	PVC pipes (25mm,110mm,20mm)
	PVC pipes (25mm,110mm,20mm)
	PVC saddles
	PVC trunking
	RJ45 connectors
	RJ45 Crimping tool
	Router if necessary
	Screw drivers
	Screws, Nut & bolts
	Side Cutters
	Soldering station, Solder wire
	SW Mounting Bracket
	Spanners
	Speakon connectors
	Spring bender
	Surge protector
	Tape measure
	Torch
	Twin surface switch
	USB-Serial adapter
	Voltage monitor
	Water pipe
	Work Suit