Hardware Installation Guide

The Operations Team must follow the steps below

PRE-INSTALLATION:
1. Technical Reconnaissance (scope site layout & choose cabinet locations)
2. Plan the project (time-line, project lead, components needed, etc)
3. Start a hardware requisition
4. Order materials/components
5. Reconcile procurement of materials with project needs
6. Modify exiting hardware:
  1. Cabinet
- Drilling and mounting of fans
  - Fan 1 Should be browing inside
  - Fan 2 Should be browing out
  - Fan 3 Should be browing inside
- Add block board to Power and server cabinets covering the entire interior back wall of the cabinet
- Wiring of the carbinet
  - Installation of battery cables
  - installation of wire to the fans
- Install Double surface Socket, AVS, AC cables to the main Switch
- Drill possitions for Charger, LVD.
  1. Power Socket
- Drill holes for speakon connectors
- Soldering and mounting of speakon connectors
  - Speakon connector should be mounted the side of the one gang switch two way switch.

HOW TO CHOOSE CABINET LOCATIONS:

Pick a central location for the Switchboard:
- Distance between cabinet & workstations should not be > 90m
- If distance between any 2 points exceed 90m add another switch cabinet

Switch
Cabinet

Choose a central location for the Server Cabinet:
- Needs to be in a well ventilated room, at least a window
- Room needs to be secure: windows with bars and door with locks

Choose a well ventilated area for the Power cabinet:
For J2's are more than 10 workstations add one more power cabinet Power Cabinet (a full back up system with 4 batteries)

CABINET DESIGNS:

Standard Design = 2 cabinets.

1
2

Power + (Switch and Server)

Alternative Design = 3 cabinets.

1
2
3

     Power + Server + Switch

CABINET LAYOUT

   NOT

Correct	Incorrect

STANDARD DESIGN
All cabinets in different rooms: see below

        Switch +	Server	+	Power
Server
3

Fan(air out)
LVD

Charger

Power Connections

Shelf

Switch

4 Batteries

Power Connections

1

2
Fan(air out)
Blockboard
Fan(air in)
Blockboard
Voltage Monitor

Fan(air out)
Blockboard

ALTERNATIVE DESIGN

Server & Switch in the same cabinet stacked vertically on top of the Power Cabinet: see below

Switch
Server

Fan(air out)

+

Blockboard
1

        Switchboard & Server

Power Connections
2

Voltage Monitor

Blockboard

Fan (air out)
LVD

3

Charger)

4 Batteries
Shelf

        Power

Fan (air in)

Fan (air out)

Blockboard

DAY OF INSTALLATION

Should be done prior to Back Data Entry by Support & Deployment Team

Alternative Back Data Entry:The Support & Deployment Team connects touch-screens to a local server and ESCOM electricity, with a working hospital generator or Baobab generator, then migrate data later.

PRIOR TO DEPARTURE:
Use the “Hardware Check-list” to confirm you have all materials needed to bring to the site.

Stage 1: RUN WIRES & PIPES

Install of cabinets
- Power
  - Should be centered in the room where installed wherever possible
- Server
  - Should be installed on top of the power cabinet
  - Incase there are in different locations with the power cabinet then it should be installed 1.5m from the ground
- Switch
  - Should be installed 2m from ground

Stage 2: INSTALL CABINETS
1. Install PVC pipe for power and network cables
2. Install PVC trunking
3. Installation of power and data sockets
Should be installed at 250cm from the ground

Stage 3:
1. Pulling cables
2. Terminate Ethernet cables
Stage 3: TEST

1. Test Power Connections with volt multimeter to make sure 48 volts are coming from each power socket.
2. Test Connectivity- (i.e. “ping” server IP addresses). Test point of care at each station.
3. Test connectivity between Baobab system & HMIS office (i.e. “ping” server IP address)
4. If site has internet, configure Baobab server on site to access Baobab HQ network.

SECURITY & SAFETY: FINAL CHECK

All cabinets must have a padlock
Padlocks should have short locking hook.
1. All rooms must be locked
2. Label keys: 1 set of with HMIS Officer & 1 set at Baobab HQ in Operations Department key cabinet
3. Every room with a power cabinet needs to have a fire extinguisher

OPERATIONS HARDWARE CHECKLIST	CHECK LIST FOR NEW SITE HW INSTALLATION
	TOOLS/ MATERIALS REQUIRED	QTY	CHECK
	Keys for server room & cabinets

	2.5mm earth wire
	48V cooling fan
	Babble level
	Batteries
	Battery Charger
	Battery Charger for drill machine
	Battery terminals

	Circuit Breaker
	server

	Drill bits ( concrete, steel, wood bits)
	Drill machines (both electric & battery power)

	Fish tape
	Hacksaw
	Hammer
	Hydrolic cutting machine
	Insulation tape

	Ladders
	LVD
	Multimeter
	Network Switch
	Padlocks for cabinets
	Plain bend
	Pliers
	Power Extension cord
	PVC coupling
	PVC Nipples
	PVC pipes (25mm,110mm,20mm)
	PVC pipes (25mm,110mm,20mm)
	PVC saddles
	PVC trunking
	RJ45 connectors
	RJ45 Crimping tool
	Router if necessary
	Screw drivers
	Screws, Nut & bolts
	Side Cutters
	Soldering station, Solder wire
	SW Mounting Bracket
	Spanners
	Speakon connectors
	Spring bender
	Surge protector
	Tape measure
	Torch
	Twin surface switch
	USB-Serial adapter
	Voltage monitor
	Water pipe
	Work Suit